## report
Sand Filter Calculations
Known Items: | Diameter | Height | [7 empty] | play sand | 3.47 | feet | inches
30 gal drum | 19.5 | 29.5 | [7 empty] | filter sand | 5.48 | 0 | 0
55 gal drum | 23.75 | 34.5 | [7 empty] | size-cu.ft. | 0.5
Cylinder Choice | [9 empty] | (for 50 lb bag)
Choose if cylinder or rectangle |  |  | cylinder |  | Enter data in green cells only
| Diameter | Height |  |  | Blue cells are results of calculations
Enter cylinder dimensions | 23.75 | 34.5 | inches |  | Yellow cells are known data and constants
Rectangle Choice
| length | width | height
Enter rectangle |  |  |  | inches |  | Calculating safe daily flow rate
Choices Regardless of Shape | [5 empty] | Enter maximum need |  | 300 | gal/day
Choose head height | 10
[6 empty] | Required sq.ft. |  | 0.84887 | sq.ft for Maximum flow
Enter size of gravel bag | 0.5 | price: | 3.47 | each |  |  |  | 1.6977 | sq.ft for minimum flow
Enter size of sand bag | 0.5 | price: | 5.48 | each
[6 empty] | Chosen sq. ft. |  | 3.0765 | safe
Choose sand Type | filter sand |  |  |  |  | There is no lower limit on flow. Lower is better.
Material List Derived from Choices:
Materials | [5 empty] | Range of safe flows
Number of gravel bags: | 2 | Sieving play sand is hard labor |  |  |  | Low flow |  | 15.1008 | Gal/hr | 0.25168 | Gal/min
Number of sand bags: | 10 | Play sand has loss from sieving it. |  |  |  | Maximum flow |  | 22.6513 | Gal/hr | 0.37752 | Gal/min
Cost of gravel: | 6.94 | Filter sand is cleaner and more uniform
Cost of sand: | 54.8 | Filter sand should be used if possible |  |  |  | Low flow |  | 60.4034 | quarts/hr | 32.2151 | oz/min
Total media cost: | 61.74 |  |  |  |  | Maximum flow |  | 90.6051 | quarts/hr | 48.3227 | oz/min
Do not exceed maximum flow rates!
Media Depth: | 24.5 | inches
Tap height from bottom: | 26 | inches | Minimum media safe height: |  |  | 15.748 | safe |  |  | Yield of Filter
[10 empty] | 362.4204 | Gal/day
Head in ft: | 0.83333 | inches | Capacity check-low flow: |  |  | 362.4204 | adequate |  |  | 543.6306 | Gal/day
pressure: | 0.36083 | PSI

## filter construction
Slow Sand Filter Calculations
Enter parameters in the green cells. Gold cells are constants.
liters/sq.meters |  |  | 10.7639 | sq. ft | 0.26417 | gals | 1 meter= | 3.2808 | ft. | 0.433 | ft head to psi
low flow | maximum | Safe limits
200 | 300 | liters/msq/hr | 2.3066 | psi /ft | from head |  | 3.7854 | Liter / gal | Enter dimensions of filter to calculate:
4.9085 | 7.3627 | gals/sq. ft/hr | [6 empty] | Diameter in feet | sq. ft surface
0.081808 | 0.12271 | gals/min/sq.ft | [6 empty] | 1.9792 | 3.0765 | sq. ft.
117.8035 | 176.7053 | gals/day/sq.ft
[9 empty] | length | width | sq. ft.
safe media depth |  |  | Best | Minimum |  | (not recommended) |  |  | 0 | 0 | 0
0.73 | 0.4 |  | 2.395 | 1.3123 | feet | for contaminated
|  |  | 28.7402 | 15.748 | inches | water sources |  |  | Safe flow rate: | round | rectangle
[9 empty] | gals/hr low flow | 15.1008 | 0
Total height: | 2.875 | feet |  | Low flow is better, but it is not the minimum rate. |  |  |  |  | gals/hr max flow | 22.6513 | 0
inches: | 34.5 | inches |  | The slower the better filtration. The max are safety |  |  |  |  | gals/min low flow | 0.25168 | 0
| Best | Minimum |  | limits and not design requirements. DO NOT |  |  |  |  | gals/min max flow | 0.37752 | 0
head height: | 0.47999 | 1.5627 | feet | Exceed the maximum rate! |  |  |  |  | gals/day low flow | 362.4204 | 0
| 5.7598 | 18.752 | inches | [5 empty] | gals/day max flow | 543.6306 | 0
Chosen head: | 10 | inches | [6 empty] | Calculate desired size of filter
media depth: | 24.5 | inches | [6 empty] | Desired flow/day |  | Liters
tap depth: | 26 | inches from bottom | [6 empty] | 300 | gals/day | 1135.62
Head in ft: | 0.83333 | ft. | [6 empty] | 0.84887 | sq. ft. high
pressure: | 0.36083 | psi | [6 empty] | 1.6977 | sq. ft. low
Calculate feet from inches:
29.5 | inches = | 2.4583 | feet
Calculate media | [6 empty] | bags
Gravel |  | 1 | cu.ft. | 0.5 | cu.ft/bag | 3.47 | 2 | 6.94
Sand |  | 5 | cu.ft. | 0.5 | cu.ft/bag
Bags |  | 10 | bags |  |  |  | Home Depot costs
play sand (loss) |  | 12.5 | bags | 3.47 | 43.375
filter sand (no loss) |  | 10 | bags | 5.48 | 54.8 | diff: | 11.425
|  | sand | chosen | 5.48
Isn’t your labor to sieve bags of sand worth spending slightly more for filter sand? Filter sand is already graded to be used in a water filter.

## measurements
|  | Date |  |  |  | Piezometer
|  | Measurements: | oz/min | gph | gpday | Inches | Notes:
8 | oz/cup | 2012-11-07 | 17 | 7.9688 | 191.25 |  | Back-flushed and started testing at 3:00 PM. Added fish water to start Schmutzdecke growing.
4 | cups/qt | 2012-11-10 | 18 | 8.4375 | 202.5 |  | Back-flushed and started testing at 12:00 PM. 3/16 orfice installed. Water is milky.
4 | qt /gal
128 | oz/gal
18 | oz/min
1080 | oz/hour
8.4375 | gal/hour
202.5 | gal/day
Convert
cups | oz
1.5 | 24